- Section 07 72 00 Roof Accessories – Series 3400 Smoke Ventilators

This document is meant as a spec guide for the discernment of technical specifications that may apply to our products and that may be chosen to apply per a customer requirement. It is not meant as a claim to all the standards listed as applicable to every Series 3400 product sold.

# GENERAL

## SUMMARY

### Section includes:

#### Automatic Smoke Ventilation Devices and Accessories

### Related Sections:

#### Section 06100 (06 10 00) - Wood Framing. Site built wood curbs and nailers.

#### Section 07310 (07 31 00) - Roof Shingles and Shakes. Flashing of skylight base.

#### Section 07320 (07 32 00) - Roof Tiles. Flashing of skylight base.

#### Section 07360 (07 3600) – Single Ply Membrane Roofing.

#### Section 07510 (07 51 00) - Built-Up Bituminous Roofing. Flashing of skylight base.

#### Section 07520 (07 52 00) - Modified Bituminous Membrane Roofing. Flashing of skylight base.

#### Section 07525 (07 5250) – Modified Sheet Roofing.

#### Section 07530 (07 53 00) - Electrometric Membrane Roofing. Flashing of skylight base.

#### Section 07540 (07 54 00) - Thermoplastic Membrane Roofing. Flashing of skylight base.

#### Section 07600 (07 60 00) - Flashing and Sheet Metal. Metal curb flashings.

#### Section 07610 (07 6100) – Sheet Metal Roofing

#### Section 08620 (08 60 00) - Unit Skylights. Skylights without reflective tube.

## REFERENCES

### Aluminum Association (AA)

#### Specifications for Aluminum Structures.

### American Architectural Manufacturers Association (AAMA)

#### AAMA 1600/IS7, Skylight Standard

#### AAMA Skylight Installation Manual

#### AAMA 1505.1-87, Voluntary Standard Uniform Load Test Procedure for Plastic Glazing Skylights by Uniform Static Air Pressure Difference.

### American Society for Testing and Materials (ASTM)

#### ASTM A463/A463M - Standard Specification for Steel Sheet, Aluminum Coated, by the Hot Dip Process.

#### ASTM A653/A653M - Standard Specification for Steel Sheet, Zinc Coated (Galvanized), by the Hot Dip Process.

#### ASTM A792/A792M - Standard Specification for Steel Sheet, 55% Aluminum-Zinc Alloy-Coated by the Hot-Dip Process.

#### ASTM B209 - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate.

#### ASTM D635 - Test Method for Rate of Burning and/or Extent of Time of Burning of Self-Supporting Plastics in a Horizontal Position.

#### ASTM D1929 - Test Method for Ignition Properties of Plastics.

#### ASTM D2843 - Standard Test Method for Density of Smoke from the Burning or Decomposition of Plastics.

#### ASTM D4802 Specification for Poly (Methyl Methacrylate) Acrylic Plastic Sheet

#### ASTM E84 - Standard Test Method for Surface Burning Characteristics of Building Materials.

#### ASTM E108 - Standard Test Methods for Fire Tests of Roof Coverings.

#### ASTM E283 - Test Method for Rate of Air Leakage Through Exterior Windows, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen.

#### ASTM E330 - Structural Performance of Exterior Windows, Curtain Walls, and Doors.

#### ASTM E331 Test Method for Water Penetration of Exterior Windows, Curtain Walls and doors by Static Air Pressure Difference.

#### ASTM E1886 - Standard Test Method for Performance of Exterior Windows, Curtain Walls, Doors, and Impact Protective Systems Impacted by Missiles and Exposed to Cyclic Pressure Differentials.

### International Building Code (2024) and International Fire Code (2024)

### National Roofing Contractors Association (NRCA)

#### Roofing and Waterproofing Manual.

### Underwriters Laboratory (UL)

#### UL 793 Standard for Heat and Smoke Vents

### Factory Mutual (FM

#### FM 4430 Standard for Heat and Smoke Vents

### National Fire Protection Association (NFPA)

#### NFPA 204 Standard for Heat and Smoke Vents

### American Welding Society (AWS)

#### AWS D1.1 Structural Welding Code

## PERFORMANCE REQUIREMENTS

### Smoke Vents shall operate automatically, in accordance with the operating requirements of UL 973.  Smoke Vents shall operate automatically by activation of a UL Listed fusible link.

#### Wind uplift:  Class 90.

#### Snow loading:  10 lbs./ft².

#### Fusible Link: Select one: [165] [212] [286] [360] [520] °F

### Light-Transmitting Plastics

#### KILON Monolithic or Prismatic polycarbonate

##### Combustion Rating:

###### CC1 for Polycarbonate

###### CC2 for Acrylic

##### Flame Spread Index: < 25

##### Smoke-development Index: < 450

### Smoke Vents shall operate automatically by activation of a UL Listed fusible link. Link temperature as required by AHJ.

## SUBMITTALS

### Submit under provisions of Section 01300.

### Product Data: Manufacturer's data sheets on each product to be used, including:

#### Product Data Sheet

#### Installation & Maintenance Manual

#### Installation instructions

### Sales Drawing showing smoke vent assembly, base, and accessories

### Certificate of Compliance

### Warranty Documents

## DELIVERY, STORAGE AND HANDLING

### Handle, deliver and store in manufacturer’s original packaging, following the manufacturer’s recommendations. Store in a dry area and in a manner to prevent damage.

### Exercise caution when hoisting unit to the roof so as not to damage the release mechanism.

## WARRANTY

### Smoke Vent Warranty: Provide written warranty by the manufacturer, agreeing to provide replacement components that exhibits defects in materials or workmanship.

### Warranty period to be 10 years from date of installation.

# PRODUCTS

## MANUFACTURERS

### Acceptable Manufacturer:  Kingspan Light + Air, 28662 N. Ballard Drive, Lake Forest, IL 60045, phone +1 (800) 759 6985, fax +1 (847) 816 0425, http://www.kingspanlightandair.us.

### Substitutions: Not permitted

### Requests for substitutions will be considered in accordance with provisions of Section 01600.

## SMOKE VENTILATORS

### SERIES 3500 SMOKE VENTS

#### Inside curb dimension to be

##### Select one: [5555:  48”x 48”] [5566:  48” x 60”] [5578:  48” x 72”] [5596:  48” x 90”] [55102:  48” x 96”]

#### UL 793 Listed smoke ventilator, Polycarbonate Double-Lid, with UL listed fusible link, link temperature as required by AHJ.  Class 90 wind uplift, 10 lbs./ft² snow loading.

##### Kingspan Light + Air Model Select one: [SLDOULTO (Drop out)] [SLDOUL (for Drop out with SF base] [ESSLDOUL (Drop out with SF base and Fusible link)] [ASLDOUL (Drop out with Retrofit Base)]

##### Finish: Manufacturer’s standard mill finish aluminum.

#### Glazing

##### Bubble dome

###### Clear monolithic Acrylic over White monolithic Acrylic

#### Mounting:

CM Mounting for SLDOUL and ASLDOUL

SF Mounting for SLDOUL and ESSLDOUL

##### Select one: [Curb Mounted (CM)] [Self-flashing (SF)]

Below options are for SF and Si mounting only.  Delete all if CM or CT

###### Aluminum

###### 9” high

###### Optional: [1” x 4” Wood Nailer (WN)]

## Accessories

### Optional: Accessories

Select one of the options below and delete the other.

#### Steel Security Bars: Optional steel security/burglar bars by Kingspan Light + Air shall be ½” steel bars welded and assembled into a 1 ½” x 1 ½” x 1/8” steel angle frame and provided with a white powder coated paint finish or approved equal.

- OR -

#### Steel mesh Safety Screen:  Optional steel 0.167” diameter resistance welded wire mesh screen.  Galvanized steel with stainless steel straps to secure to SF base or existing curb.

## FABRICATION

### Fabricated by an ISO 9001:2015 Certified Manufacturer.

### Fabricate free of visual distortions and defects. Weld corners and joints.

### All fasteners and hardware shall be corrosion resistant.

### Provide a weather tight assembly.

### Provide a UL Label in accordance with UL 793. UL Label to include:

#### Manufacturer’s name or identifying symbol.

#### Catalog or Model number.

#### The word “Caution” and the following:

##### Automatically operated Vent

##### Risk of Injury

##### Do not place anything on top of this device

#### The date or other dating period of manufacture,

#### The Class of roof deck construction.

# EXECUTION

## INSTALLATION

### Install completely assembled smoke vents with curbs in accordance with manufacturer’s instructions. Coordinate roof membrane installation requirements specified in other Sections.

### Apply bituminous paint on metal surfaces of units in contact with cementitious material and dissimilar metals.

### After installation, remove shipping strap screws and test vents to ensure that vents operate as intended.

## INSPECTION AND MAINTENANCE

### Inspect and maintain smoke vents in accordance with the requirements of the NFPA 204, Standard for Heat and Smoke Vents, 2007 Edition.

END OF SECTION